# Table of Contents

NRAD ↔ NETL TRIGA Ontology Mapping

1. Ontology Overview

1.1 NRAD Classes → Neutron OS Tables

1.2 NRAD Relationships → Neutron OS Foreign Keys

2. Sensor Mapping (Critical Path)

2.1 Control Elements

2.2 Power Measurement

2.3 Temperature

2.4 Flow

2.5 Radiation Monitoring

2.6 Other

3. Limits Schema (Gap Analysis)

3.1 Proposed sensor_limits Table

3.2 Example Data (from NRAD)

3.3 Limit Checking Query

4. Analysis Integration (ML/SM Models)

4.1 NRAD Analysis Nodes

4.2 Neutron OS models Table Mapping

5. Data Flow Comparison

5.1 NRAD Data Flow (Graph Edges)

5.2 Neutron OS Data Flow (dbt Lineage)

5.3 Hybrid Integration Point

6. Gaps to Address in Neutron OS

7. Recommended Actions

Immediate (This Week)

Short-term (2-4 Weeks)

Medium-term (1-2 Months)

Appendix: Full NRAD Measurements File Columns

# NRAD ↔ NETL TRIGA Ontology Mapping

Purpose: Compare INL's NRAD Digital Twin ontology with our NETL TRIGA schema to identify alignment opportunities and gaps.

Source: nrad_dt_generic_ontology_v4.txt (Ryan via Nick & Cole, January 2026)

## 1. Ontology Overview

### 1.1 NRAD Classes → Neutron OS Tables

| NRAD Class | Count | Neutron OS Equivalent | Notes |
| --- | --- | --- | --- |
| Digital Twin | 1 | reactors table | Root entity |
| Control Element | 3 | control_rods table | Shim 1, Shim 2, Regulating |
| Detector | 25+ | sensors table | Most of the ontology |
| Limits | 12 | NEW: `sensor_limits` | Critical gap in our schema |
| Data Acquisition System | 1 | data_sources table | TINA system |
| Data File | 4 | data_files / Bronze layer | CSV ingestion |
| Analysis | 2 | models table | ML Operation, SM Operation |
| Visualization | 1 | Superset dashboards | Not in DB schema |
| Modes of Operation | 1 | NEW: `operational_modes` | Data collection, prediction |
| Remote Monitoring | 0* | remote_access_logs | Not used in ontology |

*Remote Monitoring class exists but has no records.

### 1.2 NRAD Relationships → Neutron OS Foreign Keys

| NRAD Relationship | Usage | Neutron OS Equivalent |
| --- | --- | --- |
| consists_of | 40 | reactor_id FK on sensors |
| sends_data_to | 35 | Data lineage (dbt refs) |
| has_setting_limits | 25 | sensor_id FK on limits |
| allows | 3 | Mode → capability mapping |

## 2. Sensor Mapping (Critical Path)

### 2.1 Control Elements

| NRAD Name | NRAD Properties | NETL TRIGA Equivalent | Tag Name |
| --- | --- | --- | --- |
| Shim Rod 1 | position (in), 0-24 range | Safety Rod | TBD |
| Shim Rod 2 | position (in), 0-24 range | Shim Rod | TBD |
| Regulating Rod | position (in), 0-24 range | Regulating Rod | TBD |

Key Properties to Map:

{
  "current position": 24,
  "least reactive position": 24,
  "most reactive position": 0,
  "has LCO requirements": "True",
  "magnet switch activated": "False"
}

### 2.2 Power Measurement

| NRAD Name | Type | NETL TRIGA Equivalent |
| --- | --- | --- |
| Multi-Range Linear Channel 1 | Ionization chamber, % Power | NI-1 (NP-1000) |
| Multi-Range Linear Channel 2 | Ionization chamber, % Power | NI-2 (NP-1000) |
| Multi-Range Linear Channel 3 | Ionization chamber, % Power | NI-3 (NP-1000) |
| Wide-Range Log Channel | Fission counter, % Power + period | NI-4 (Wide Range) |

### 2.3 Temperature

| NRAD Name | Units | NETL TRIGA Equivalent |
| --- | --- | --- |
| Fuel Temperature Detector | °C | IFE Thermocouple |
| Heat Exchanger Inlet Temperature | °C | Pool outlet temp |
| Heat Exchanger Outlet Temperature | °C | Pool inlet temp |
| Reactor Tank Temperature | °C | Pool bulk temp |
| Demineralizer Inlet/Outlet Temperature | °C | (Not directly measured) |

### 2.4 Flow

| NRAD Name | Units | NETL TRIGA Equivalent |
| --- | --- | --- |
| Primary Cooling System Flow | gpm | Primary flow |
| Secondary Cooling System Flow | gpm | Secondary flow |
| Demineralizer Flow | gpm | Demin flow |

### 2.5 Radiation Monitoring

| NRAD Name | Type | Units | NETL TRIGA Equivalent |
| --- | --- | --- | --- |
| Reactor Room RAM | Gamma monitor | R/h | ARM (Area Radiation Monitor) |
| Reactor Room Air Particulate Monitor | CAM | DPM/ft³ | CAM |
| Reactor Room Gross-Gaseous Monitor | CAM | DPM/ft³ | (Combined with CAM) |
| Demineralizer RAM | Gamma monitor | mR/h | Demin monitor |
| East Radiography Station Foil RAM | Radiation monitor | mR/h | N/A (no radiography) |
| North Radiography Station Foil RAM | Radiation monitor | mR/h | N/A |
| North Radiography Station Cell RAM | Radiation monitor | mR/h | N/A |

### 2.6 Other

| NRAD Name | Type | NETL TRIGA Equivalent |
| --- | --- | --- |
| Reactor Tank Water Level | Water level monitor, ft-in | Pool level |
| Scram Button | Boolean | SCRAM input |

## 3. Limits Schema (Gap Analysis)

This is the most valuable part of the NRAD ontology for Neutron OS.

### 3.1 Proposed sensor_limits Table

CREATE TABLE gold.sensor_limits (
    limit_id UUID PRIMARY KEY,
    sensor_id UUID REFERENCES sensors(sensor_id),
    
    -- Limit definition
    limit_type VARCHAR(100),           -- 'High temperature', 'Low water level', etc.
    limit_operator VARCHAR(20),        -- 'Greater than', 'Less than', 'Between', 'Boolean'
    limit_value JSONB,                 -- Flexible: number, string, array
    limit_units VARCHAR(20),
    
    -- Logic for multi-channel (e.g., "2 out of 3")
    required_logic VARCHAR(20),        -- '2 of 3', '3 of 3', NULL for single
    
    -- Regulatory classification
    safety_importance VARCHAR(50),     -- 'Safety limit', 'LCO', 'Scram function', 'Operational limit'
    reference VARCHAR(200),            -- 'TSR-406 pg. 17', 'SAR-406 pg 3-16'
    
    -- Metadata
    created_at TIMESTAMP DEFAULT NOW(),
    updated_at TIMESTAMP,
    created_by VARCHAR(100)
);

### 3.2 Example Data (from NRAD)

INSERT INTO gold.sensor_limits VALUES
-- Fuel Temperature Safety Limits
(gen_random_uuid(), '<fuel_temp_sensor_id>', 
 'High temperature, cladding less than 500 C', 'Greater than', '1150', '°C',
 NULL, 'Safety limit', 'TSR-406 pg 16', NOW(), NULL, 'system'),

(gen_random_uuid(), '<fuel_temp_sensor_id>',
 'High temperature, cladding greater than 500 C', 'Greater than', '950', '°C',
 NULL, 'Safety limit', 'TSR-406 pg 16', NOW(), NULL, 'system'),

-- Multi-Range Linear Channel Scram Functions
(gen_random_uuid(), '<nmp1_sensor_id>',
 'High power level', 'Greater than or equal to', '120', 'Percent Power',
 '2 of 3', 'Scram function', 'SAR-406 pg. 6-10', NOW(), NULL, 'system'),

(gen_random_uuid(), '<nmp1_sensor_id>',
 'Low voltage limit', 'Less than', '300', 'V',
 '2 of 3', 'Scram function', 'SAR-406 pg. 6-10', NOW(), NULL, 'system'),

-- Reactor Tank LCO
(gen_random_uuid(), '<tank_level_sensor_id>',
 'Low water level limit', 'Less than', '"10, 3"', 'ft, in',
 NULL, 'LCO', 'TSR-406 pg. 23', NOW(), NULL, 'system');

### 3.3 Limit Checking Query

-- Check all sensors against their limits
WITH current_readings AS (
    SELECT sensor_id, value, timestamp
    FROM silver.sensor_readings
    WHERE timestamp > NOW() - INTERVAL '1 minute'
),
limit_violations AS (
    SELECT 
        cr.sensor_id,
        sl.limit_type,
        sl.safety_importance,
        cr.value AS current_value,
        sl.limit_value,
        sl.limit_operator,
        CASE 
            WHEN sl.limit_operator = 'Greater than' AND cr.value::float > sl.limit_value::float THEN TRUE
            WHEN sl.limit_operator = 'Less than' AND cr.value::float < sl.limit_value::float THEN TRUE
            WHEN sl.limit_operator = 'Greater than or equal to' AND cr.value::float >= sl.limit_value::float THEN TRUE
            ELSE FALSE
        END AS is_violated
    FROM current_readings cr
    JOIN gold.sensor_limits sl ON cr.sensor_id = sl.sensor_id
)
SELECT * FROM limit_violations WHERE is_violated = TRUE;

## 4. Analysis Integration (ML/SM Models)

### 4.1 NRAD Analysis Nodes

{
    "name": "ML Operation Prediction",
    "class_name": "Analysis",
    "properties": {
        "type": "LSTM",
        "feature_variables": [
            "shim_rod_1_position", 
            "shim_rod_2_position", 
            "regulating_rod_1_position", 
            "NRAD_RX_Hx_Inlet_Th"
        ],
        "target_variables": [],
        "file_type": "pickle"
    }
}

### 4.2 Neutron OS models Table Mapping

CREATE TABLE gold.models (
    model_id UUID PRIMARY KEY,
    model_name VARCHAR(100),
    model_type VARCHAR(50),            -- 'LSTM', 'Gaussian process regression', 'XGBoost'
    
    -- Feature/target mapping
    feature_variables JSONB,           -- Array of sensor names or tag names
    target_variables JSONB,            -- What the model predicts
    
    -- Model storage
    model_artifact_path VARCHAR(500),  -- S3/MinIO path to pickle/ONNX
    model_version VARCHAR(20),
    
    -- Metadata
    trained_at TIMESTAMP,
    training_data_range TSTZRANGE,     -- Time range of training data
    metrics JSONB,                     -- {'rmse': 0.05, 'r2': 0.95}
    
    -- Lineage
    created_by VARCHAR(100),
    created_at TIMESTAMP DEFAULT NOW()
);

## 5. Data Flow Comparison

### 5.1 NRAD Data Flow (Graph Edges)

Detectors → TINA DAQ → CSV File → Analysis → Results File → UI
    │                      │
    │                      └── Direct to UI (real-time display)
    │
    └── has_setting_limits → Limits

### 5.2 Neutron OS Data Flow (dbt Lineage)

Sensors → Redpanda → Bronze (raw) → Silver (typed) → Gold (curated) → Superset
    │                    │              │                │
    │                    │              │                └── ML Training
    │                    │              │
    │                    │              └── Limit checking
    │                    │
    │                    └── Anomaly detection
    │
    └── sensor_limits (static reference)

### 5.3 Hybrid Integration Point

┌─────────────────────────────────────────────────────────────────────────────┐
│                         SYNC POINT: Asset Registry                          │
├─────────────────────────────────────────────────────────────────────────────┤
│                                                                             │
│   DEEPLYNX                              NEUTRON OS                          │
│   ┌──────────────────┐                  ┌──────────────────┐               │
│   │  Ontology        │                  │  Iceberg Tables  │               │
│   │  ┌────────────┐  │    Sync every    │  ┌────────────┐  │               │
│   │  │ Detector   │  │◀──── 1 hour ────▶│  │  sensors   │  │               │
│   │  │ nodes      │  │                  │  │  table     │  │               │
│   │  └────────────┘  │                  │  └────────────┘  │               │
│   │  ┌────────────┐  │                  │  ┌────────────┐  │               │
│   │  │ Limits     │  │◀──── Sync ──────▶│  │sensor_limits│ │               │
│   │  │ nodes      │  │   (bi-directional)│  │  table     │  │               │
│   │  └────────────┘  │                  │  └────────────┘  │               │
│   └──────────────────┘                  └──────────────────┘               │
│                                                                             │
│   Real-time state                       Historical analysis                 │
│   Limit checking (graph)                Trend analysis (SQL)                │
│   WebSocket to UI                       Superset dashboards                 │
│                                                                             │
└─────────────────────────────────────────────────────────────────────────────┘

## 6. Gaps to Address in Neutron OS

| NRAD Has | Neutron OS Status | Action |
| --- | --- | --- |
| Limits with safety importance | ❌ Missing | Add sensor_limits table |
| SAR/TSR reference citations | ❌ Missing | Add reference column |
| Required logic (2 of 3) | ❌ Missing | Add required_logic column |
| Modes of Operation | ❌ Missing | Add operational_modes table |
| ML model definitions | ⚠️ Partial | Enhance models table |
| Tag name mapping | ⚠️ Partial | Add tag_name to sensors |

## 7. Recommended Actions

### Immediate (This Week)

Add `sensor_limits` table to Gold schema

Map NETL TRIGA sensors to NRAD-compatible structure

Add `safety_importance` and `reference` columns

### Short-term (2-4 Weeks)

Implement limit checking dbt model

Create `operational_modes` table

Define sync format for DeepLynx ↔ Neutron OS

### Medium-term (1-2 Months)

Propose unified ontology to INL

Build bi-directional sync proof-of-concept

Document in shared schema spec

## Appendix: Full NRAD Measurements File Columns

From the ontology's Data File node:

NRAD_RX_Rx_ON          -- Reactor on/off status
NRAD_RX_NMP1_PWR       -- Multi-range channel 1 power
NRAD_RX_NMP2_PWR       -- Multi-range channel 2 power
NRAD_RX_NMP3_PWR       -- Multi-range channel 3 power
NRAD_RX_PERIOD         -- Reactor period
NRAD_RX_SHIM1_POS      -- Shim rod 1 position
NRAD_RX_SHIM2_POS      -- Shim rod 2 position
NRAD_RX_REG_POS        -- Regulating rod position
NRAD_RX_SHIM1_CV       -- Shim rod 1 control voltage
NRAD_RX_SHIM2_CV       -- Shim rod 2 control voltage
NRAD_RX_REG_CV         -- Regulating rod control voltage
NRAD_RX_Tank_Temp_T1   -- Tank temperature
NRAD_RX_Hx_Inlet_Th    -- Heat exchanger inlet temperature
NRAD_RX_Pri_Flow       -- Primary flow

These map directly to time-series columns in our Bronze layer.

Document created: January 15, 2026 Based on: nrad_dt_generic_ontology_v4.txt